End User Customer Requirements for terminating Wholesale Services

The End User must:

1.  Provide adequate conduit from the right-of way into the building, confirm

access facilities to the building are available for fiber provisioning.

Conduit from the right-of-way to the building is the customer’s responsibility. If no conduit exists or space in existing conduit is not sufficient, the installation will not proceed.

It is the customer’s responsibility to locate private Utilities on your premises should construction be required. Construction will not proceed until this is complete.

CONDUIT SPECIFICATIONS: One 2 inch schedule 40 PVC conduit from 2 ft below grade at the building exterior to a pull box on the building exterior. Pull Box to have a minimum dimension of 12inch x 12inch x 6 inches deep. Place one 2 inch conduit sleeve through wall from pull box to the inside of the equipment room.

Conduit must be equipped with 400 lb rated pull tension. Equip conduit with no more than 2 rigid galvanized sweeps between cable pulling points. It is the responsibility of the customer to seal the conduit after installation to protect from damage such as water.

2.  Provide adequate backboard space in equipment demarcation room.

The customer will provide minimum of one 4 x 4 ft plywood backboard, 4 x 8 ft preferred, in equipment demarcation room.   Ensure adequate clearance of 36-inch in front of backboard.  If the fiber demark is within 25 feet of the equipment rack, a wall board will not be required; all hardware and terminations will be installed in the customer provided rack.   Access to MGN or ground bus, with a run length of no more than 30 ft. is needed.  Standard connectors (e.g., lug) should be supported for CenturyLink’s connection.

Non Stand Alone Bldgs. (IE:multi-tenent/strip malls): If shared Building Terminal  supporting this location does not have adequate space for local telephone company fiber termination, customer or building owner will need to provide a 24” x 24” x 9” ventilated cabinet with ¾” plywood. This cabinet needs to be associated next to the original building terminal, to support association of shared DEMARC facilities.

3.  Ensure the demarcation point is in an accessible and environmentally controlled location (i.e. Multi-tenant buildings):

The CENTURYLINK Equipment requires a clean, dust free environment that is environmentally controlled to temperatures of 55-80 degrees Fahrenheit and humidity of 70% or less.

If you are in a Multi-tenant building ensure that the CENTURYLINK demarcation point, (the location where the Local Phone Company wires enter your building), is accessible to the CENTURYLINK technician.  You may need to coordinate access with the building manager to ensure that access is available on the day of installation.  Ensure that this location remains dry and free of dampness, and the room temperature needs to remain within the tolerance of sensitive electronic hardware.

4.  Ensure four (4) consecutive Rack Units of space in a 19” data rack are required for Enhanced Service:

It is the customer’s responsibility to provide space in a 19” wide data rack for the Ethernet hardware.  CENTURYLINK will not install the hardware on a shelf or the floor.  The rack may be either wall or floor mounted.

5.  Provide dedicated power outlet and Common Ground:

The CENTURYLINK termination electronics are powered by customer provided 120 VAC (20 Amp) circuit. CENTURYLINK requires the outlet to be a three prong, non-GFCI duplex, dedicated and grounded electrical outlet within six (6) feet of the equipment location.  If the outlet is in a public area, a single plug must be provided so other equipment cannot be plugged into the outlet.  Common ground must be 25 ohm or less. If the customer does not have a UPS on the AC, service will be lost in the event of an AC power failure.  If UPS is required, customer will provide such arrangement.

6.  Complete inside wiring work.

Inside wiring must be completed by the customer prior to the arrival of the CENTURYLINK installation technician.  Customer must extend the wiring from the demarcation point to their suite or office location where the Ethernet service will be used.  If copper, a minimum of Cat 5e cable is needed with a maximum of 328 ft run to the equipment.  If fiber, then the cable must match the handoff ordered on the ASR.  Fiber slack storage needs to be on the customer side of the cable, not at the demarcation.

7.  Confirm Ethernet Hand-Off requirements:

CENTURYLINK will provide a copper or optical termination as ordered by the Carrier on the ASR requesting the service.   The type needs to be coordinated with your Carrier.  Options include standard RJ-45 Copper Ethernet connection, Multimode or Single mode Fiber connections.

8.  If applicable, confirm that any planned LAN connections have an appropriate Ethernet port available:

The customer needs to ensure a suitable port is available to provide the network functionality they desire and within distance of Ethernet specifications.  Customer will program Ethernet port for appropriate speed and full duplex setting (No auto-sense). It is the customer’s responsibility to provide a cable(s) to connect you LAN to the CENTURYLINK Ethernet equipment.  Customer will provide an appropriate Ethernet patch cable for connecting CENTURYLINK demarcation and Customer Provided Equipment.

9.  CENTURYLINK Ethernet product is a Layer 2 network service only.   All customer premise Local Area Network (LAN) Layer 3 (e.g. IP) addressing is the responsibility of the customer.  CENTURYLINK will provide pricing for additional equipment/labor to enable Layer 3 functionality.

In most cases this will need to be a router/switch which will provide the layer 3 routing of subnets and VLAN on the customer’s network.  If the customer only requires layer 2 bridging (a flat network) across the Ethernet service then a standard Ethernet switch port is all that is required.

10. The CENTURYLINK installer will not connect the Ethernet service to the LAN.

- Our installers will install the hardware and identify a port for your connection.

- CENTURYLINK highly recommends the use of a qualified networking vendor to assist you with your LAN configuration.

11. Access

- CenturyLink requires an emergency customer contact for access 24 hours a day, 7 days a week.

CENTURYLINK provides fiber termination and the Ethernet transceiver.

CenturyLink provides fiber termination, fiber patch panel, Ethernet transceiver

(if needed), Ethernet DEMARC device and power surge strip.

CenturyLink provides fiber termination, fiber patch panel, Ethernet transceiver

(if needed), Ethernet DEMARC device and power surge strip.